## System comparison
| Step 4 | A: cost + CO2 | B: CO2 only | A: cost + CO2 vs Step 4 [%] | B: CO2 only vs Step 4 [%]
heat [MWh] | 3070.399 | 3070.399 | 3070.399 | 0 | 0
CO2 [t] | 34.606 | 23.841 | 23.155 | -31.105 | -33.089
fuel/electricity cost [EUR] | 44319.336 | 44823.612 | 45031.225 | 1.138 | 1.606
var O&M cost [EUR] | 9101.808 | 9090.355 | 9087.865 | -0.126 | -0.153
operating cost [EUR] | 53421.144 | 53913.967 | 54119.09 | 0.923 | 1.306
annualised capex [EUR] | 34743.271 | 34743.271 | 34743.271 | 0 | 0
economic cost [EUR] | 88164.414 | 88657.237 | 88862.361 | 0.559 | 0.792
CO2 cost [EUR] | 4637.148 | 3194.76 | 3102.751 | -31.105 | -33.089
economic cost + CO2 cost [EUR] | 92801.563 | 91851.997 | 91965.111 | -1.023 | -0.901
CO2 intensity [kg/MWh delivered] | 12.065 | 8.312 | 8.073 | -31.105 | -33.089
economic cost per MWh delivered [EUR/MWh] | 30.737 | 30.909 | 30.981 | 0.559 | 0.792

## Heat per unit group
| Step 4 | A: cost + CO2 | B: CO2 only
heat pumps (P0 + P4) | 2900.494 | 2910.004 | 2910.136
biomass boiler | 30.899 | 2.98 | 0.038
electric boiler | 134.613 | 153.327 | 153.615
gas boiler | 4.393 | 4.087 | 6.609

## CO2 per unit group
| Step 4 | A: cost + CO2 | B: CO2 only
heat pumps (P0 + P4) | 18.713 | 18.774 | 18.775
biomass boiler | 12.335 | 1.19 | 0.015
electric boiler | 2.719 | 3.098 | 3.103
gas boiler | 0.838 | 0.78 | 1.261

## Units Step4 reference
| capacity [MW] | heat [MWh] | share of heat [%] | full-load hours [h] | hours at max capacity [h] | fuel/electricity cost [EUR] | var O&M cost [EUR] | operating cost [EUR] | annualised capex [EUR] | CO2 [t] | CO2 cost [EUR] | economic cost [EUR] | economic cost + CO2 cost [EUR]
heat pump station | 0.2 | 1449.732 | 47.216 | 7248.661 | 5639 | 18455.275 | 4450.678 | 22905.952 | 16035.255 | 9.353 | 1253.317 | 38941.208 | 40194.524
biomass boiler | 0.013 | 30.899 | 1.006 | 2355.683 | 2187 | 849.256 | 64.269 | 913.525 | 697.995 | 12.335 | 1652.891 | 1611.52 | 3264.411
electric boiler | 0.132 | 134.613 | 4.384 | 1019.123 | 236 | 6104.576 | 127.883 | 6232.459 | 1589.854 | 2.719 | 364.407 | 7822.313 | 8186.72
gas boiler | 0.09 | 4.393 | 0.143 | 48.582 | 3 | 436.697 | 5.139 | 441.836 | 384.911 | 0.838 | 112.326 | 826.747 | 939.073
heat pump supermarket | 0.2 | 1450.762 | 47.25 | 7253.81 | 5619 | 18473.533 | 4453.839 | 22927.372 | 16035.255 | 9.36 | 1254.207 | 38962.627 | 40216.834
TOTAL | 0.636 | 3070.399 | 100 |  |  | 44319.336 | 9101.808 | 53421.144 | 34743.271 | 34.606 | 4637.148 | 88164.414 | 92801.563

## Units scenario A
| capacity [MW] | heat [MWh] | share of heat [%] | full-load hours [h] | hours at max capacity [h] | fuel/electricity cost [EUR] | var O&M cost [EUR] | operating cost [EUR] | annualised capex [EUR] | CO2 [t] | CO2 cost [EUR] | economic cost [EUR] | economic cost + CO2 cost [EUR]
heat pump station | 0.2 | 1454.424 | 47.369 | 7272.121 | 5672 | 18458.334 | 4465.082 | 22923.417 | 16035.255 | 9.383 | 1257.373 | 38958.672 | 40216.045
biomass boiler | 0.013 | 2.98 | 0.097 | 227.229 | 196 | 81.919 | 6.199 | 88.118 | 697.995 | 1.19 | 159.438 | 786.113 | 945.551
electric boiler | 0.132 | 153.327 | 4.994 | 1160.799 | 227 | 7400.004 | 145.66 | 7545.665 | 1589.854 | 3.098 | 415.066 | 9135.518 | 9550.585
gas boiler | 0.09 | 4.087 | 0.133 | 45.202 | 1 | 406.312 | 4.782 | 411.094 | 384.911 | 0.78 | 104.51 | 796.005 | 900.515
heat pump supermarket | 0.2 | 1455.58 | 47.407 | 7277.901 | 5650 | 18477.042 | 4468.631 | 22945.673 | 16035.255 | 9.391 | 1258.373 | 38980.929 | 40239.301
TOTAL | 0.636 | 3070.399 | 100 |  |  | 44823.612 | 9090.355 | 53913.967 | 34743.271 | 23.841 | 3194.76 | 88657.237 | 91851.997

## Units scenario B
| capacity [MW] | heat [MWh] | share of heat [%] | full-load hours [h] | hours at max capacity [h] | fuel/electricity cost [EUR] | var O&M cost [EUR] | operating cost [EUR] | annualised capex [EUR] | CO2 [t] | CO2 cost [EUR] | economic cost [EUR] | economic cost + CO2 cost [EUR]
heat pump station | 0.2 | 1456.994 | 47.453 | 7284.972 | 5706 | 18495.547 | 4472.973 | 22968.519 | 16035.255 | 9.4 | 1259.595 | 39003.775 | 40263.37
biomass boiler | 0.013 | 0.038 | 0.001 | 2.903 | 1 | 1.047 | 0.079 | 1.126 | 697.995 | 0.015 | 2.037 | 699.121 | 701.158
electric boiler | 0.132 | 153.615 | 5.003 | 1162.98 | 227 | 7437.736 | 145.934 | 7583.671 | 1589.854 | 3.103 | 415.846 | 9173.524 | 9589.371
gas boiler | 0.09 | 6.609 | 0.215 | 73.097 | 6 | 657.061 | 7.733 | 664.793 | 384.911 | 1.261 | 169.007 | 1049.705 | 1218.712
heat pump supermarket | 0.2 | 1453.142 | 47.327 | 7265.711 | 5617 | 18439.835 | 4461.146 | 22900.981 | 16035.255 | 9.375 | 1256.265 | 38936.236 | 40192.501
TOTAL | 0.636 | 3070.399 | 100 |  |  | 45031.225 | 9087.865 | 54119.09 | 34743.271 | 23.155 | 3102.751 | 88862.361 | 91965.111

## Hours at capacity
| Step 4 | A: cost + CO2 | B: CO2 only
heat pump station | 5639 | 5672 | 5706
biomass boiler | 2187 | 196 | 1
electric boiler | 236 | 227 | 227
gas boiler | 3 | 1 | 6
heat pump supermarket | 5619 | 5650 | 5617

## Merit order
unit | tCO2 per MWh heat | fuel/electricity [EUR/MWh heat] | var O&M [EUR/MWh heat] | CO2 cost [EUR/MWh heat] | Step 4 (fuel + O&M) | A: cost + CO2 | B: CO2 only
heat pump station | 0.006 | 12.375 | 3.07 | 0.865 | 15.445 | 16.309 | 0.865
biomass boiler | 0.399 | 27.485 | 2.08 | 53.494 | 29.565 | 83.059 | 53.494
electric boiler | 0.02 | 38.749 | 0.95 | 2.707 | 39.699 | 42.406 | 2.707
gas boiler | 0.191 | 99.417 | 1.17 | 25.572 | 100.587 | 126.159 | 25.572
heat pump supermarket | 0.006 | 12.375 | 3.07 | 0.865 | 15.445 | 16.309 | 0.865

## Emission factors
carrier | ef_tCO2_per_MWh_input | biogenic | source
electricity | 0.02 | FALSE | Uniper, El och klimat: Swedish production mix ~20 g CO2/kWh
biomass | 0.4032 | TRUE | IPCC 2006 Vol.2 Ch.2 Table 2.2, Wood/Wood Waste 112,000 kg/TJ
gas | 0.19656 | TRUE | IPCC 2006 Vol.2 Ch.2 Table 2.2, Other Biogas 54,600 kg/TJ (biomethane)

## Sens carbon price
carbon price [EUR/t] | CO2 [t] | economic cost [EUR] | CO2 cost [EUR] | heat pumps (P0 + P4) | biomass boiler | electric boiler | gas boiler
0 | 34.606 | 88164.414 | 0 | 2900.494 | 30.899 | 134.613 | 4.393
25 | 32.957 | 88193.434 | 823.933 | 2903.268 | 26.732 | 136.187 | 4.212
50 | 27.774 | 88389.173 | 1388.709 | 2906.042 | 13.169 | 147.003 | 4.185
100 | 24.131 | 88623.997 | 2413.101 | 2908.948 | 3.706 | 153.658 | 4.087
134 | 23.841 | 88657.237 | 3194.76 | 2910.004 | 2.98 | 153.327 | 4.087
200 | 23.695 | 88680.064 | 4739.065 | 2910.136 | 2.6 | 153.576 | 4.087
300 | 23.68 | 88683.23 | 7104.123 | 2910.136 | 2.56 | 153.615 | 4.087
500 | 23.155 | 88862.361 | 11577.428 | 2910.136 | 0.038 | 153.615 | 6.609

## Sens biogenic CO2
| A: cost + CO2, biogenic = 0 | B: CO2 only, biogenic = 0 | A: cost + CO2, biogenic counted (main) | B: CO2 only, biogenic counted (main)
heat pumps (P0 + P4) | 2910.004 | 2146.927 | 2910.004 | 2910.136
biomass boiler | 31.001 | 114.902 | 2.98 | 0.038
electric boiler | 124.895 | 16.531 | 153.327 | 153.615
gas boiler | 4.498 | 792.038 | 4.087 | 6.609
economic cost [EUR] | 88170.871 | 153195.294 | 88657.237 | 88862.361
CO2 incl. biogenic [t] | 34.532 | 211.203 | 23.841 | 23.155
CO2 fossil/electricity only [t] | 21.297 | 14.185 | 21.872 | 21.878

## Monthly heat S
date | heat pump station | biomass boiler | electric boiler | gas boiler | heat pump supermarket | unserved heat | demand
2019-01-01 | 148.164 | 8.195 | 36.69 | 1.482 | 148.2 | 0 | 342.731
2019-02-01 | 133.913 | 7.543 | 41.31 | 2.363 | 133.463 | 0 | 318.592
2019-03-01 | 142.395 | 4.635 | 13.196 | 0.047 | 142.412 | 0 | 302.685
2019-04-01 | 127.642 | 1.202 | 2.179 | 0 | 128.576 | 0 | 259.599
2019-05-01 | 110.525 | 0.22 | 3.784 | 0 | 112.667 | 0 | 227.196
2019-06-01 | 92.711 | 0 | 4.887 | 0 | 94.845 | 0 | 192.443
2019-07-01 | 96.415 | 0 | 0 | 0 | 92.832 | 0 | 189.247
2019-08-01 | 97.194 | 0 | 0 | 0 | 98.438 | 0 | 195.632
2019-09-01 | 106.433 | 0.043 | 0.002 | 0 | 103.488 | 0 | 209.966
2019-10-01 | 118.24 | 0.378 | 0.553 | 0 | 121.005 | 0 | 240.176
2019-11-01 | 130.006 | 2.71 | 7.221 | 0.012 | 130.232 | 0 | 270.181
2019-12-01 | 146.094 | 5.973 | 24.791 | 0.488 | 144.605 | 0 | 321.95

## Monthly heat A
date | heat pump station | biomass boiler | electric boiler | gas boiler | heat pump supermarket | unserved heat | demand
2019-01-01 | 148.164 | 1.214 | 43.976 | 1.176 | 148.2 | 0 | 342.731
2019-02-01 | 133.913 | 1.209 | 47.644 | 2.363 | 133.463 | 0 | 318.592
2019-03-01 | 142.527 | 0.097 | 17.603 | 0.047 | 142.412 | 0 | 302.685
2019-04-01 | 127.838 | 0 | 2.985 | 0 | 128.776 | 0 | 259.599
2019-05-01 | 113 | 0 | 0.569 | 0 | 113.627 | 0 | 227.196
2019-06-01 | 94.4 | 0 | 0 | 0 | 98.043 | 0 | 192.443
2019-07-01 | 96.415 | 0 | 0 | 0 | 92.832 | 0 | 189.247
2019-08-01 | 97.194 | 0 | 0 | 0 | 98.438 | 0 | 195.632
2019-09-01 | 106.433 | 0 | 0.045 | 0 | 103.488 | 0 | 209.966
2019-10-01 | 118.44 | 0 | 0.799 | 0 | 120.937 | 0 | 240.176
2019-11-01 | 130.006 | 0.075 | 9.856 | 0.012 | 130.232 | 0 | 270.181
2019-12-01 | 146.094 | 0.386 | 29.85 | 0.488 | 145.133 | 0 | 321.95

## Monthly heat B
date | heat pump station | biomass boiler | electric boiler | gas boiler | heat pump supermarket | unserved heat | demand
2019-01-01 | 148.182 | 0.001 | 44.384 | 1.982 | 148.182 | 0 | 342.731
2019-02-01 | 133.766 | 0.037 | 47.644 | 3.535 | 133.61 | 0 | 318.592
2019-03-01 | 142.544 | 0 | 17.603 | 0.144 | 142.394 | 0 | 302.685
2019-04-01 | 129.632 | 0 | 2.985 | 0 | 126.982 | 0 | 259.599
2019-05-01 | 113.259 | 0 | 0.437 | 0 | 113.5 | 0 | 227.196
2019-06-01 | 92.213 | 0 | 0 | 0 | 100.231 | 0 | 192.443
2019-07-01 | 96.194 | 0 | 0 | 0 | 93.053 | 0 | 189.247
2019-08-01 | 99.48 | 0 | 0 | 0 | 96.153 | 0 | 195.632
2019-09-01 | 106.778 | 0 | 0.045 | 0 | 103.142 | 0 | 209.966
2019-10-01 | 117.65 | 0 | 0.799 | 0 | 121.727 | 0 | 240.176
2019-11-01 | 131.455 | 0 | 9.87 | 0.074 | 128.782 | 0 | 270.181
2019-12-01 | 145.841 | 0 | 29.85 | 0.873 | 145.386 | 0 | 321.95